#### Health, Safety & Environment Committee

Subject:	University Fire Officer’s Report

- Fire Incidents

There have been no fire incidents in the current reporting period.

- Malicious Activations of the fire alarm systems in Halls of Residence

Manual Call Pont Activations

We are at present suffering a spate of malicious activations of the fire alarm systems in a number of Halls. 35 in total to date, since the start of the academic year (October-07)

Location of Malicious Activations

1 David Collett

1 Butler Court

2 in Towers (of which incorporated the attendance of the fire & rescue service)

9 spread about the village blocks (3 Cayley, 3 Whitworth, 1 Telford, 1 Faraday, 1 Rutherford)

But more alarming 22 in Elvyn Richards Courts

Letters have been sent to all occupants residing in Halls on Campus informing them that

the University doesn’t view the above activity as ‘larking about’ or ‘high spirits’ and reminding all that, to tamper with the fire alarm system irrespective of any disciplinary action the University may impose is a CRIMINAL ACT WHICH CARRIES PROSECUTION

The malicious activations can only be caused, by residents, their guests, or by allowing intruders into Halls, by failing to maintain security to the entrance of the buildings.

Concern that students will start to ignore the fire alarm signals and assume that it is another prank is becoming a high risk in Elvyn Richards.

The Health & Safety Office advised imago Services to consider installing a temporary CCTV system in Residential Halls in an attempt to identify the culprit(s)

The last correspondence from Imago Services informed the H & S Office that a demo of a covert camera by SDC had occurred on the 30th of January and there are now purchasing a mobile covert camera to assist in these matters.

3.	Evacuation chair

University security staff training on the C Max stair climber is now completed.

Time trials in responding to selected buildings across campus have been conducted. All evacuations of a person at a refuge point (an area of relative safety providing protection to occupants from fire and smoke for a minimum 30 minutes) to a place of (ultimate safety, out side the building, assembly point and alike) were completed well within the allocated time of 30 minutes.

The times recorded below were from the moment the call was made to LU Security gate-house requesting for the evac chair to a given location on campus to the completion of the evacuation of a person to ultimate safety (out side of the building)

List of buildings of the controlled evacuation

Sir Richard Morris building 2nd Floor	11 Minutes

Sir David Davis building 2nd Floor	15 Minutes

Sir Dennis Rooke building 1st Floor	15 Minutes

Stewart Miller building 3rd Floor	15 Minutes

S building 2nd Floor	19 Minutes

Wolfson building 2nd Floor	18 Minutes

Pilkington Library 3rd Floor	15 Minutes

Chemistry building 5th Floor	25 Minutes

Schofield building 3rd Floor	13 Minutes

Haslegrave 	17 Minutes

LUSAD (Main Building)	12 Minutes

- Fire Evacuations Tests on University Buildings (conducted Nov-07)

Overall most evacuation times were achieved, however there were a few buildings that failed to achieve an acceptable time for a safe evacuation. This was mainly due to

staff or students questioning the fire alarm and delaying their response to the evacuation, or absent Fire Marshals to instruct occupants to evacuate and assemble at the designated fire assembly point my have contributed to this.

All persons that assembled at the designated assembly points were reminded on the need to evacuate the building immediately once the fire alarm has been heard and to treat all fire alarm signals as a genuine fire emergency.

It was also noted that during the evacuation test, some staff using lecture theatres / rooms in certain buildings were unfamiliar with the local fire procedures for that particular building. Staff/lectures were reminded of their responsibility for the safety of their students, and to insure they make them selves aware of the fire action emergency procedures and the location of the fire assembly point to the particular build in use

The use of alternative means of escape appeared not to be used in some buildings this tendered to be due to inadequate supervision from staff to students, visitors and guests, leading to a strong tendency for overuse of the buildings main entrances.

List of buildings that failed the controlled evacuation time

Sir David Davies (W Building)	Evacuation time 8 Min 0 Sec

Safe Evacuation time 3 Minutes 30 Seconds

Edward Herbert Building		Evacuation time 4 Min 30 Sec

Safe Evacuation time 3 Minutes 30 Seconds

Herbert Manzoni Building		Evacuation time 4 Min 20 Sec

Safe Evacuation time 3 Minutes 30 Seconds

5.	Departments that still have insufficient fire marshal representation within academic buildings

The need for departments to nominate fire marshals to improve the management procedures of all occupants, in the event of a fire emergency in the buildings below is still required.

BUILDING 					DEPARTMENTS

Edward Herbert Building			Imago Services, SDC

Action to date:- Fire marshal training by the DSO of Imago services is ongoing

Stewart Miller Building			Aeronautical & Automotive Engineering

Action to date:- Arrangements are being made by the DSO for the H& S Office to conduct a fire marshal training course in-house

6. 	Fire Alarm Activations and Fire Service call-outs.

In the last 4 month period the Fire Service have been called to 14 activations 0 of which resulted in being an actual fire (see table below)

|  | Oct 07 | Nov 07 | December 07 | January 08 |
| --- | --- | --- | --- | --- |
| Number of Activations | 97 Residential 8 Academic | 65 Residential 7 Academic | 28 Residential 1 Academic | 38 Residential 7 Academic |
| Activations involving Fire Service | 5 Towers East Towers West Towers West Towers East Elvyn Richards | 5 Towers West 2 Towers West 13 SU Main Building Towers West 11 Towers West 1 | 3 Towers West 13 ECB Houses Towers West 20 | 1 Telford 11 |
| Genuine Fire Activations | 0 | 0 | 0 | 0 |

###### ACADEMIC BUILDINGS FIRE ALARM ACTIVATIONS

Sir David Davis	0	Holywell Park	3		Haslegrave		0

Brockington 		0	Stewart Mason	0	Pilkington Library	0

Business School	1	Sir John Ferguson	0	Wolfson		2

Schofield		1	Hockey pavilion	0	Hi Pack		2

Chemistry		1	Keith Green		0	Wavy top		0

Stewart Miller		1	Students Union	1	Sir Frank Gibb		0

11 Holywell		0	Innovations Cent	0	Performance Cent	2

S Building		0	Dan Maskel		0	Netball/Badminton	0

Victory Hall		1	Imago Sales		2	Loughborough Pk	3

Sir David Wallace	2	EHB			3	LUSAD		1

Hockey Pavilion	1	Swimming Pool	2	Herbert Manzoni	1

###### ACCOMMODATION FIRE ALARM ACTIVATIONS

Faraday 		15	Falkner / Eggington	38	Elvyn Richards	49

Butler Court		9	Towers		11	Telford			24

Royce			17	Hazlerigg / Rutland	4	Whitworth		7

Cayley			28	David Collett	 	3	Rutherford		9

Burleigh Court		2	Towers Bungalow	1	High fields ECB	1

Unite			0

The major causes of fire alarm activations in Halls of Residence are

- 49 Unattended cooking in self catering kitchens

- 70 Steam from showers in en-suite bedrooms and aerosol sprays

- 15 Faulty sensors

- 16 Unknown causes

- 29 Other

- 37 Malicious call point activations (all in Halls)

- 3 Smoking incident

LOCATIONS OF COOKING RELATED INCIDENTS IN THE HALLS

Faraday 		4	Falkner / Eggington		19	Elvyn Richards	3

Butler Court		5	Towers			0	Telford			9

Royce			2	Hazlerigg/Rutland		0	Whitworth		2

Cayley			2	David Collett			0	Rutherford		3

Burleigh Court		0

(All above information gathered from period 01/09/07 –31/01/08) R M Harrison –Health, Safety & Environment Office

Date – February 2008

Copyright © Loughborough University.. All rights reserved.