#### Health, Safety & Environment Committee

Subject:  University Fire Officer’s Report

- Fire Incidents

There has been one fire incident in the current reporting period:

Monday, 1st October 2008 Students Union Purple Onion – fire in Papa Simon’s

The fire alarm signal was received in the Security gatehouse on the BOLD system at 05:57 a.m. Two security officers responded immediately and confirmed flames issuing out of the ventilation grill to the catering outlet.

The Fire & Rescue Service was called, two pumps and crews arrived on site at 06:08 a.m. the fire was extinguished at approximately 06:30 a.m

At 08:15 a.m the building was confirmed safe and the Fire & Rescue Service stood down.

The seat of the fire was in the catering outlet (kebab shop) known as Papa Simon’s. This unit was damaged internally by fire & smoke with slight smoke damage affecting the adjoining Students’ Union shop

The building was unoccupied at the time and nobody was hurt.

The building was later proved to be structurally sound and normal business in the adjoining Students’ Union shop and around the student village area was reinstated

There has been no confirmed cause of the fire, and an investigation into the cause of the fire is now underway.

If there are any lessons to be learned from the incident it illustrates the benefits of having fire alarms linked to the Security Gatehouse and monitored 24/7. While the fire damage is significant, the building is salvageable and the adjacent shop could be up and running quite soon. Estates are working through a priority list composed from fire risk assessments which will ensure that eventually all significant University buildings are protected in this way.

2.	New Automatic Fire Alarm Systems

The following buildings:-

Brockington, Brockington Ext, James France, Martin Hall, S building, W building, Wolfosn building, Wolfosn Annex, Schofield building, Graham Oldham, Holywell Houses 3 & 7

Have during this reporting period been fitted throughout with Automatic Fire Detection systems (AFDs) and are all now fully operational. Currently digicoms (hard wear linked to the fire alarm panel) are being fitted to all of the above fire alarm panels and  once fitted the digicom will send a signal directly to the security gate house should a activation occur.  This shall provide a 24/7 early warning that a fire may be occurring in one of these buildings and allow an out of hours investigation during none operational/working hours by the university security staff.

Where necessary all fire marshals and the weekly testing staff have received instruction on the new fire alarm panels.

3.	Refuge Communication Systems

Refuge communication systems have been installed in the following buildings:-

Brockington Ext, James France, Martin Hall, S building, W building, Wolfosn building.

These systems are directly linked to the security gate house. If a refuge call point is activated a signal will be received in the LU security gate house identifying the location of a person waiting at a refuge point for assistance. Security trained staff will then respond with the C-Max evacuation chair to vertically evacuate the occupant out of the building should that person be in immediate danger. The system will also allow 2-way communication between the person waiting at the refuge point and the security gate house allowing continuous contact to update and reassure any person waiting at the refuge

Training for the use of this equipment in the security gate house for security personal has been arranged to be conducted on 22nd October 2008 by a representative form Deaf Alerter plc

4. 	Fire Alarm Activations and Fire Service call-outs.

In the last 4 month period the Fire Service have been called to 3 activations none of which resulted in being an actual fire (see table below)

|  | June 08 | July 08 | Aug 08 | Sept 08 | Total |
| --- | --- | --- | --- | --- | --- |
| Number of Activations | 34 Residential 5 Academic | 16 Residential 14 Academic | 22 Residential 10 Academic | 30 Residential 14 Academic | 102 43 |
| Activations involving Fire Service | Towers West Towers West Holywell Pk | 0 | 0 | 0 | 3 |
| Genuine Fire Activations | 0 | 0 | 0 | 0 | 0 |

###### Academic Buildings Fire Alarm Activations

Holywell Park	8	Chemistry		5	Sir John Ferguson	4

Swimming Pool	1	Business School	4	Sir David Wallace	1

EHB			5	Rutland		2	John Clements	1

Haslegrave		1	Hi-Pac		1	Ashby Rd		1

Imago Sales Office	1	James France 	1	Keith Green		1

Innovations		1	Hazlerigg		5

###### Accommodation Fire Alarm Activations In Lu Halls Of Residence

Faraday 			  9	Falkner / Eggington	  25	Elvyn Richards	  5

Butler Court			10	Towers		    1	Telford		15

Royce				12	Whitworth		    1	Cayley		10

David Collett	 		  1	Rutherford		    9	Burleigh Court	  3

Faraday/Royce D/Hall	  1

###### Accommodation Fire Alarm Activations In Other Managed Halls Of Residence

Unite			  17

Derwent Living	  0

The Major Causes Of Fire Alarm Activations In Lu Halls Of Residence

- 25 Unattended cooking in self catering kitchens

- 30 Steam from showers in en-suite bedrooms and aerosol sprays

- 14 Faulty sensors

- 20 Unknown causes

- 1 Other (water contamination in detector head, sensors removed/damaged etc.)

- 8 Malicious call point activations (all in Halls)

- 1 Accidental activation of call point

- 2 Smoking incident (including Candles & incense sticks)

- 1 Contractors (dust or fumes from paint)

Locations Of Cooking Related Incidents In Lu Halls Of Residence

Faraday 		4	Falkner / Eggington		6	Elvyn Richards	0    Butler Court		2	Towers			0	Telford		4    Royce			4	Whitworth			1	Cayley		2

David Collett		0	Rutherford			2	Burleigh Court	0

Author – R Harrison

Date – October 2008

Copyright © Loughborough University.  All rights reserved.