#### Health, Safety & Environment Committee

Subject:  University Fire Officer’s Report October 2009

1.	Fire alarm installation update

Further installation of automatic fire detection systems (AFDs) in university buildings has occurred since the last report. The buildings concerned are :- Stewart Miller, Sir Frank Gibb Building, Sir Frank Gibb Laboratories, John Pickford, John Hardie, Facilities Management (office/workshops/stores). This work is now complete. Work has commenced on the following building and should be completed by November Paula Ratcliff Athletics Pavilion & Admin II/Student Services. These installations have improved the means of warning for occupants in the buildings and also provide better asset protection for all large buildings across campus. Upgrading the AFD in LUSAD buildings remains under review pending decisions about future use.

Refuge alerter communication systems have now been installed in the majority of temporary refuges accommodating persons with mobility disabilities in buildings above or below the access level.

2.	Fire marshal refresher training

It has been four years since the training of fire marshals began.  At present there are 300+ trained fire marshals available in most of the buildings across campus.  All fire marshals who received training in 2005 – to the first half of 2006 have now been contacted and asked to book on one of four refresher training sessions scheduled in 2009/2010.  A further four initial fire marshal training sessions have also been scheduled in 2009/2010.  Courses can be booked through Professional Development.

3. 	Fire Alarm Activations and Fire Service call-outs.

In the last 4 month period the Fire Service have been called to 3 activations 0 of which involved an actual fire (see table below)

|  | June 09 | July 09 | Aug 09 | Sept 09 | Total |
| --- | --- | --- | --- | --- | --- |
| Number of Activations | 47 Residential 16 Academic | 35 Residential 15 Academic | 14 Residential 10 Academic | 34 Residential 14 Academic | 130 55 |
| Activations involving Fire Service | Holywell Pk Holywell Pk | Towers West |  |  | 2 |
| Genuine Fires | 0 | 0 | 0 | 0 |  |

###### Academic Buildings:

Holywell Park		10	Graham Oldham	1	Business School	0

Sir Frank Gibb		  0	James France 	3	Power Base		0

Rutland Hall (old)	  8	S Building		6	Martin Hall		5

Hockey Pavilion	  0	Sir David Davies	1	John Cooper		1

HEBs			  5	Brockington		7	Hazlerigg old		4

Brockington Ext	  1	Wolfson		1	John Cooper		1

Michael Pearson	  2

###### Halls Of Residence( University Managed)

Faraday 			14	Falkner / Eggington	   2	E/R 50 blocks		  8

Butler Court			11	Towers		   2	Telford			12

Royce				11	Whitworth		   8	Cayley			15

David Collett	 		  7	Rutherford		   5	Burleigh Court		11

Faraday/Royce D/Hall	  	  2	UPP Blocks		 15	200 Ashby Rd		  0

Cayley/Rutherford D/Hall	  2	Elvyn Richards D/Hall	   2	David Collett D/Hall	  2

William Morris D/Hall		  1

###### Halls Of Residence (Not managed by the University)

Unite			47

The Major Causes Of Fire Alarm Activations In LU Halls Of Residence:

- 19 Unattended cooking in self catering kitchens

- 31 Steam from showers in en-suite bedrooms and aerosol sprays

- 19 Faulty sensors or fire alarm panels

- 27 Unknown causes

- 14 Other (water contamination in detector head, lighting strike, power outage etc.)

- 9 Malicious call point activations or tampering/removing of detector heads

- 2 Accidental activation of call point

- 1 Smoking incident (including Candles & incense sticks)

- 8 Contractors (dust or fumes from paint)

Cooking Related Incidents In LU Halls Of Residence:

Faraday 	2	Falkner / Eggington		  1	Elvyn Richards 50 	 0

Butler Court    	1	Towers			  0	Telford			 0

Royce		0	Whitworth			  2	Cayley			 3

David Collett	1	Rutherford			  3	Faraday/Royce D/Hall	 2

UPP		4

(All above information gathered from period 01/06/09 –30/9/09) R M Harrison –Health, Safety & Environment Office