#### Health, Safety & Environment Committee

Subject:  University Fire Officer’s Report February 2010

## 1.	Fire Incidents

There have been no fire incidents in the current reporting period:

2.	Annual controlled fire evacuations

This year the annual fire evacuations have highlighted once again that staff and students are still not fully aware of the Universities fire procedures.  This was more evident in buildings that house lecture theatres and teaching rooms.

Areas of concern witnessed

Occupants questioned the fire alarm?

Occupants took considerable time in gathering personal belongings before evacuating?

Exited the building and went else where, rather than reporting to the assembly point?

Travelled through the building to evacuate rather than leaving by the nearest exit?

Students were left to fend for themselves by lectures/staff

Congregated at the entrance to the building rather than assembling at the designated assembly point

Entered the building whilst the fire alarm was still sounding

Fire doors left wedged open

Recommendations

To prevent delays in evacuating University buildings, it is imperative that both staff and students:-

- Respond immediately when the fire alarm is sounded

- Exit the building promptly by the nearest available fire exits

- Once outside the building proceed towards the designated fire assembly point allocated to the building.

- Wait at the fire assembly point until instruction is given by the fire marshal or security officers.

Lecturers are reminded to:-

- Ensure they understand the university fire action procedures’ (fire action procedures and floor plans showing the location of the fire assembly points are placed in all lecture rooms)

- Ensure they know the location of the fire assembly point assigned to the building they are lecturing in (signage showing the location of the assembly point in relation to the building has been placed in all lecture rooms)

- Know the whereabouts of all available exits

3. 	Fire Alarm Activations and Fire Service call-outs.

In the last 4 month period the Fire Service have been called to 2 activations 0 of which involved an actual fire (see table below)

|  | Oct 09 | Nov 09 | Dec 09 | Jan 10 | Total |
| --- | --- | --- | --- | --- | --- |
| Number of Activations | 76 Residential 13 Academic | 47 Residential 7 Academic | 26 Residential 10 Academic | 34 Residential 17 Academic | 188 47 |
| Activations involving Fire Service |  |  | 1 | 1 | 2 |
| Genuine Fires | 0 | 0 | 0 | 0 | 0 |

###### Academic Buildings:

Holywell Park		4	EIS/Gymnastics	1	Clyde Williams		2

Martin Hall		2	Rutland Hall (old)	1	John Cooper			1

Chemistry		4	James France 	2	Sir David Wallace	            2

S Building		2	Swimming Pool	1	Sir David Davies	            2   Business School	4	Hazlerigg old		3	Unsteady Fluids		1

Wolfson		1	LUSAD Fine Art	1         	Burleigh Court			1

Sir Frank Gibb		1	Sportpark		3	High Performance Cent	2

###### Dining Halls:

Cayley/R-ford D/Hall		  1	Faraday/Royce D/Hall	  1	David Collett D/Hall	0

Elvyn Richards D/Hall	   	  1	William Morris D/Hall	  1	EHB			1

###### Halls Of Residence( University Managed)

Butler Court			  7	Cayley			25	David Collett	 	6

Falkner / Eggington	   	26	Faraday 		17	Royce			14 Rutherford		   	11	Telford			14	Towers		9

UPP Blocks			42	University Lodge	  3	Whitworth		9

200 Ashby Rd		  	  0

###### Halls Of Residence (Not managed by the University)

Unite

Harry French			43	William Morris		34	Holt			4

Note only 13 activations at Harry French had no visible cause/reason to activate

The Major Causes Of Fire Alarm Activations In LU Halls Of Residence:

- 62 Unattended cooking in self catering kitchens

- 2 Dining Halls

- 61 Steam from showers in en-suite bedrooms and aerosol sprays

- 12 Faulty sensors or fire alarm panels

- 19 Unknown causes

- 11 Other (water contamination in detector head, lighting strike, power outage etc.)

- 20 Malicious call point activations or tampering/removing of detector heads

- 2 Accidental activation of call point

- 1 Smoking incident (including Candles & incense sticks)

- 3 Contractors (dust or fumes from paint)

Cooking Related Incidents In LU Halls Of Residence:

Butler Court    		  3	Cayley				6     	David Collett		0

Falkner / Eggington	12	Faraday 			5     	Royce			6

Rutherford		  5 	Telford				3	Towers		0

UPP			17	Whitworth			3	University Lodge	2

(All above information gathered from period 01/10/09 –31/2/10) R M Harrison –Health, Safety & Environment Office