FACILITIES MANAGEMENT POLICY

Policy for the Water Storage and Distribution Facilities of

Buildings on Ca

mpus in Order to Prevent and Control Legionella Bacteria

Reference No. POL1.0001

Version No. 01

Effective from			Nov 2011

Review required before	Nov 2014

Author	Claire Collier

| Approved | Signed | Date |
| --- | --- | --- |
| Director of FM |  |  |
| Health, Safety and Environment Manager |  |  |

CONTENTS

|  | Page number |
| --- | --- |
| 1.0 PURPOSE | 3 |
| 2.0 SCOPE | 3 |
| 3.0 REFERENCES | 3 |
| 4.0 DEFINITIONS | 4 |
| 5.0 RESPONSIBILITIES | 5 |
| 6.0 CONTROL PRINCIPLES | 9 |
| 7.0 DOCUMENT MANAGEMENT | 14 |
| 8.0 VERSION CONTROL | 15 |

1.0 PURPOSE

This Policy is to ensure that the risks of Legionellosis are assessed, controlled, and managed in accordance with current UK Regulations, (The Control of Legionella Bacteria in Water Systems), commonly known as the Approved Code of Practice, L8. This policy should be read in conjunction with all references within this document.

This document replaces Annex O to Loughborough University Facilities Management (FM) Health and Safety Policy.

2.0 SCOPE

This policy applies to all areas and installations on the Loughborough University site for which Facilities management is responsible for the delivery of water systems to the building. This includes residential areas operated by imago services, UPP & Unite and any other organisation residing within the site where water is used or stored, and in particular to:

- Hot and Cold Water Systems

- Water systems incorporating an evaporative cooling tower or evaporative condenser.

- Any other plant and systems containing water, which is likely to exceed 20( C and which may release a spray or aerosol during operation or maintenance.

3.0 REFERENCES

The control of Legionella bacteria in water systems, APPROVED CODE OF PRACTICE & GUIDANCE. ISBN0-7176-1772-6 and references therein.

The Notification of Cooling Towers and Evaporative Condensers                  Regulations (1992).

Health and Safety at Work etc Act (1974).

COSHH Regulations (1999).

Management of Health and Safety at Work Regulations 1999

The Safety Representatives and Safety Committees Regulations                    1977.

Health and Safety (Consultation with Employees) Regulations 1996.

PRO1.0001 Written Scheme for Prevention and Control of Legionellosis

Policy on the Reporting of Accidents, Dangerous Occurrences and Occupational Ill Health.

Commissioning Checklist

Change Control Procedure

4.0 DEFINITIONS

Legionellosis – Legionnaires’ disease is a potentially fatal pneumonia caused predominantly by the Legionella pneumophila bacteria. It is the most well-known and serious form of a group of diseases known as Legionellosis. Other similar (but usually less serious) conditions include Pontiac fever and Lochgoilhead fever. Infection is caused by breathing in small droplets of water contaminated by the bacteria. The disease cannot be passed from one person to another. Everyone is potentially susceptible to infection but some people are at higher risk e.g. those over 45 years of age, smokers and heavy drinkers, those suffering from chronic respiratory or kidney disease, and people whose immune system is impaired.

Persons exposed to Legionella can develop initial symptoms such as high fever, chills, headaches, and muscle pains. Other symptoms can include diarrhoea or vomiting and delirium. The disease can be treated effectively with antibiotics in early course. Legionella bacteria can survive under a wide variety of environmental conditions although the temperature range 20C to 45C tend to favour growth. The organisms do not readily multiply below 20C and will not survive above 60C. Legionella also requires a supply of nutrients to multiply. Sources include organisms in the water such as algae, amoebae, and other bacteria. The presence of sludge, sediment, scale and other material within systems can harbour bacteria and can provide favourable conditions and protection from biocides for bacteria to survive. It is therefore incumbent that water systems are adequately maintained and cleaned / disinfected regularly. Cfu/l stands for Colony forming unit per litre of water tested.

Written Scheme Procedure  – A site specific technical document, which defines the control measures and procedures to maintain efficient and effective control of its water systems, for ongoing compliance with current UK Regulations, (The Control of Legionella Bacteria in Water Systems), commonly known as the Approved Code of Practice, L8.FM Document ref PRO1.001.

5.0 RESPONSIBILITIES

5.1 Organagram

The following Organagram indicates the lines of responsibilities relating to the Management & Control of Legionella Bacteria in water systems.

This is a pictorial representation of the lines of communication between those with responsibility.

Fig 1

5.2 Roles

There are a number of roles which are undertaken at Loughborough university in the management of Legionella Bacteria

Vice Chancellor – Loughborough University Duty Holder - a person on whom the statutory duty falls.

Director of Facilities Management (FM) - A person appointed by Loughborough University to take managerial responsibility for the overall execution of this policy.

FM Duty Holder -  A person appointed by the Director of FM in writing, to take managerial responsibility for the implementation of FM policy and procedures at the University in accordance with L8 (Part 1 Section 39).

FM Nominated Deputy  - A person appointed by the Duty Holder in writing to take managerial responsibility for the implementation of policy and procedures as specified.

Water Hygiene Management Service Provider  – A company specialising in Water Hygiene Services, contracted to provide a service to the site. The contract is established and administered in conjunction with the Duty Holder and the service provider.

Project Manager: A person/s appointed to manage the construction of new buildings and refurbishment of existing installations.

FM Helpdesk: The department responsible for receiving calls and processing maintenance works instructions for remedial works

Health, Safety and Environment Manager – A person who is responsible for advising on all matters Health, Safety and Environment and liaising with medical officers in the event of an outbreak.

Deans of Schools - A person appointed by the company to take managerial responsibility for the overall execution of this policy with respect to the processes within their departments that are not managed by FM.

Operations Managers (Nominated Responsible Persons) -  A person appointed by the Dean of School in writing, to take managerial responsibility for the implementation of FM policy and procedures with respect to the processes in their department at the University in accordance with L8 (Part 1 Section 39) that are not managed by FM.

Schools Nominated Deputy  - A person appointed by the Operations Manager to take managerial responsibility for the implementation of policy and procedures as specified .

Associated Company Director – Section or Tennant eg Sports Development Centre, Tenants etc - A person appointed by the company to take managerial responsibility for the overall execution of policy with respect to the processes within their departments that are not managed by FM.

Associated Company Manager  - Nominated Responsible Persons -  A person appointed by the Director in writing, to take managerial responsibility for the implementation of policy and procedures with respect to the processes in their department or business at the University in accordance with L8 (Part 1 Section 39) that are not managed by FM.

Associated Company -  Nominated Deputy  - A person appointed by the Associated Company Manager to take managerial responsibility for the implementation of policy and procedures as specified.

Head of Companies (Tenants) - A person appointed by their company to take managerial responsibility for the overall execution of their own Legionella Management policy with respect to the processes within their departments that are not managed by FM under their tenancy agreement.

Tennant Manager  - Nominated Responsible Persons -  A person appointed by the Tennant Comapny in writing, to take managerial responsibility for the implementation of their own legionella management policy and procedures with respect to the processes in their department at the University in accordance with L8 (Part 1 Section 39).

5.3 Responsibilities

Director of FM will:

Appoint and ensure the competency of the Duty Holder, by ensuring that the person has suitable ability, experience, training and resources to enable them to carry out the role.

Check content and guidance of this Policy and the Written Scheme.

Ensure that these are available and accessible for all persons with responsibilities under this policy.

Any modifications to this policy are carried out in consultation with the Duty Holder and the Health, Safety and Environment Manager.

FM Duty Holder will:

Review and update this Policy when appropriate in line with site procedures.

Appoint and ensure competency of FM Nominated Deputies by ensuring that the person has suitable ability, experience, training and resources to enable them to carry out the role.

Ensure all cooling towers and evaporative condensers are registered with the Local Authority. (Any changes to be notified in writing within one month of the change), as cited in the current Statutory Instrument 1992 No 2225 (The Notification of Cooling Towers and evaporative Condensers Regulations 1992), Sections 1 to 4.

Ensure Risk Assessments are reviewed on a bi-annual basis or whenever it is reasonable to suspect it is no longer valid, as cited in the current HSE L8 document, (Part 1 Section 27).

Ensure procedures listed in the Risk Assessment to manage risk are in place and that actions identified for minimising the risk listed in the Risk Assessment are reviewed and actions undertaken accordingly and recorded.

Communicate by whatever means suitable, information to the employees with regards to relevant information on the risks and control measures being undertaken to control Legionella bacteria, as cited in the current HSE L8 document, (Part 1 Section 36).

Ensure that there is a clear and concise route for notification of positive samples and clarity on who decides remedial actions and who is responsible for carrying these out.

Inform the Health, Safety and Environment Manager of positive Legionella test results over 100,000-cfu/L or sero group 1 greater than 1000 cfu/.

Chairing appropriate legionella management reviews and forums.

Undertake periodic review and ensure that an independent audit of this policy and associated written scheme is undertaken. This review should also include the policy and procedures of other key department and tenants.

Check any modifications or changes to existing installations are carried out under the site change control process and that all associated drawings, Risk Assessments and testing schedules are updated.

FM Nominated Deputies (s) will:

Take day-to-day responsibility for controlling any identified risk from Legionella bacteria in line with the Written Scheme reference PRO1.0001.

Take day-to-day responsibility for controlling any identified risk with respect to any changes to the operation of plant or the management of change process within their area.

Advise the Duty Holder of any changes or items for concern in their area.

There will be Nominated deputies identified for specific functions and operations identffied in the Written procedures. These will include, but not be limited to:

Nominated Deputy – FM Maintenance

Nominated Deputy – FM Projects

Nominated Deputy – Residential

Where one or more organisations or departments/sections operate in an area, there will be the appropriate corresponding number of Nominated Deputies

Nominated Deputy - FM Maintenance

Carry out audits to ensure all Risk Assessments are in place, completed and comply with current regulations, as cited in the current HSE L8 document, (Part 1 Section 27).

Review the Risk Assessment and control measures whenever there is a reason to suspect that they are no longer valid. i.e. when an area of the building is taken out of use. See L8 Part One, Section 38.

Ensure immediate action in response to out of specification results. Where required, ensure that equipment is removed from service until a satisfactory result is achieved.

Ensure that all scheduled control measures are in place and effective.

Ensure that the water systems operate under the conditions detailed in the Risk Assessment.

Ensure that all planned PPM work and remedial works undertaken is carried out on time, to specification and are recorded.

Create work orders and raise notifications for remedial work

Appoint suitably qualified Water Treatment Service Providers to undertake the specified maintenance and monitoring as agreed with the Duty Holder. To monitor the performance of the Service Providers through regular reviews and audits.

Ensure that a water treatment contract is in place for cooling towers, with a pre qualified and competent contractor.

Ensure that contract performance reviews are carried out on a regular basis where suitable Key Performance Indicators (KPI) will be used to improve all aspects of the contract.

Check any modifications or changes to existing installations are carried out under the site change control process and that all associated drawings, Risk Assessments and testing schedules are updated.

Nominated Deputy – FM Projects:

Ensure that the Project Manager has checked that his designers and installers are complying with Section 6.1 CONTROL PRINCIPLES “Design and Installation” for details.

Ensure that the Project Manager provides interim measures for all new and refurbished systems prior to beneficial occupation.

Following any modification to a water system, ensure that the Project Manager has obtained a completed Legionella Commissioning Check list from the installer, reviewed and signed off in conjunction with the designer.

Ensure that the Project Manager has obtained from the designer completed drawings, Legionella Risk Assessments and testing schedules on all new water systems.

Ensure that the Project Manager has checked any modifications or changes to existing installations are carried out under the site change control process and that all associated drawings, Risk Assessments and testing schedules are updated and forwarded to the Nominated Deputy.

Nominated Deputy - Residential

Ensure that all scheduled control measures are in place and effective.

Water Hygiene Management Service Provider will:-

Have a suitable and sufficient management structure to ensure professional competence at all times.

Ensure that appropriate task-based risk assessments are carried out prior to commencing works.

Ensure that all their personnel i.e. Specialist Water Treatment Contractors, Specialist Mechanical Contractors and Consultants are competent, and suitably trained certificated and experienced, and have the necessary equipment to carry out their duties in line with the Written Scheme. (PRO1.0001)

Be registered with the Legionella Control Association or equivalent.

Complete work schedules within an agreed timeframe.

Provide day-to-day advice on control of Legionella.

Communicate all bacteria test results to the FM Maintenance team by written communication.

Provide corrective recommendations immediately, in the event of an out of compliance issue.

Inform the FM Maintenance if physical access or operations cannot be completed, and record on a spreadsheet.

FM Helpdesk will:

Process maintenance works instructions for remedial works following routine monitoring by the Water Hygiene management Service provider.

FM Project Managers will:

Ensure that the appointed designers and installers are complying with Section 6.1 CONTROL PRINCIPLES “Design and Installation” .

Ensure that interim control measures for all new and refurbished systems prior to beneficial occupation are implemented.

Following any modification to a water system, ensure that appropriate information is handed over in accordance with the Written Scheme.

Health, Safety and Environment Manager will:-

Work with site Occupational Health Centre Staff to carry out effective assessment of individuals from test positive areas who report adverse health effects consistent with Legionellosis and appropriate referral of such individuals requiring specialist advice.

Advise site management, in writing, the requirement to report such cases under RIDDOR legislation.

Carry out liaison with Medical Officers for Environmental Health (MEOH) in the event of an outbreak.

In the event of an outbreak, liaise with the Local Council Environmental Health Dept.

6.0 CONTROL PRINCIPLES

6.1 Design and Installation

6.1.1 Water Systems:

All water systems shall be designed, manufactured and installed to be safe and with out risks to health when used at work.  Adequate documentation shall be provided to the user to ensure that the system can be maintained and operated safely and without risk to health when used at work from Legionella in conjunction with ACOP L8.

Designers will ensure that water service systems comply with the Water Supply (Water Fittings) Regulations 1999.

Designers will ensure that general issues of design, sizing, layout, construction and commissioning of water systems comply with BS6700 and subsequentially BS EN 806 when published.

Materials and fittings are acceptable for use in the water system are listed in the directory published by the Water Research Centre.

Low corrosion materials (copper, plastic, stainless steel etc) should be used where practicable.

Non-metallic materials are deemed to be compliant provided they meet with the appropriate British Standard, BS 6920:’Suitability of non-metallic products for use in contact with water intended for human consumption with regard to their effect on the quality of water’.

Certain aspects of the system will have to comply with the Building Regulations. Water storage tanks should be fitted with covers, which comply with the Water Supply (Water Fittings) Regulations 1999 and insect screens fitted to any pipe work open to the atmosphere, e.g. the overflow pipe.

Modifications or changes to existing installations should always be carried out under appropriate change control.

All associated drawings, Legionella Risk Assessments and testing schedules are updated by the designer/ UKFM Compliance Co-ordinator before hand over.

Ensure that all new systems have completed drawings, Risk Assessments and testing schedules.

6.1.2 Calorifiers:

The storage capacity and recovery rate of calorifers should be selected to meet the normal daily fluctuations in the hot water use without any drop in the supply temperature.

6.1.3 Storage Tanks:

Multiple linked tanks should be avoided wherever possible, if this cannot be done then equal draw off the tanks should be achieved.

All cold water head tanks should be designed to contain a maximum supply of 24 hours usage.

6.1.4 Cooling Towers:

Cooling Tower systems should be designed and constructed to BS4485, or demonstrate that the construction of the tower is both suitable and sufficient for operation within the UK.

All equipment is designed and constructed to comply with L8 with respect to operation, cleaning and maintenance.

All cooling tower installations shall have a fully automated control and dosing system as part of the design of the system where possible.

Cooling Towers shall be subject to a water treatment programme. The treatment principles will be as defined with the Written Scheme Procedure.

All Cooling Towers and evaporative condensers shall be registered with the Local Authority in accordance with Statutory Instrument 1992 No 2225 (The Notification of Cooling Towers and evaporative Condensers Regulations 1992), Sections 1 to 4 before being connected in service.

Any modification or change to the following details of existing cooling towers or evaporative condensers shall be notified to the Local Authority in writing within 1 month of the change being made.

Consideration should be taken into account regarding the system volume / system dynamics to evaluate the half-life of the system.

6.2 Risk Management

All Risk Assessments shall be carried out by approved competent persons.

Such Competent persons shall be able to demonstrable competence and experience of Risk Assessment.

Risk assessments shall identify recommendations according to the following criteria:

- Any remedial works that may be required to ensure the system meets the current L8 “Approved Code of Practice & Guidance” legislation.

- Identify scheduled maintenance checks/tasks and records that shall be adhered to in order to comply with current legislation and reduce the risk to an acceptable level.

Risk assessments should include an up-to-date line diagram of the system and consideration of the population at risk should also be made.

The risk assessment shall be reviewed whenever there is reason to believe that it is no longer valid (e.g. due to changes in plant, equipment, water usage patterns, new information about risks or control measures, or based on water testing results etc), as cited in L8 Part One, Section 38.

All systems likely to contain water between 20 - 45° C, and which may release a spray or aerosol during normal operation/maintenance shall not be operated until a suitable Risk Assessment on the system has been performed, and recommended control measures put in place.

The Risk Assessment and control measures shall be reviewed in any event at least every 2 years. Reviews of the assessment shall be documented and filed with the original Risk Assessment, as cited in L8 Part One, Section 38.

All cooling tower Risk Assessments shall include a statement on the physical condition and location of the cooling tower.

Where the Risk Assessment demonstrates that risks are insignificant, no control measures are necessary.

Maintenance personnel involved with water systems should be aware of and understand the need for appropriate PPE requirements

6.3 Equipment Identification

All cooling towers, calorifiers, humidifiers, showerheads, and other relevant plant identified by the Risk Assessment(s) shall be registered and labelled, where possible, with unique “Plant Item Numbers”.

A ‘site register’ shall be maintained of all Calorifiers, Shower Heads and sentinel monitor points.

6.4 Maintenance and Sampling

All maintenance and routine sampling shall be carried out in accordance with L8 and managed in accordance with specific risk assessments. Specific activities and frequency is detailed in the Written Scheme Procedure (PRO1.0001)

Sampling shall be undertaken as per The British Standards Institution BS7592; 1992 (Methods for sampling legionella organisms in water and related matters).

Undertake analysis in accordance with ISO 11731/1998 (British Standard 6068 water quality detection and enumeration of Legionella), at a UKAS accredited registered Laboratory.

6.5 Incident Reporting

The following action shall be taken based on the Legionella Bacteria test results:

- Cooling Towers

| Results | Action |
| --- | --- |
| < 100 cfu/l | Check system, dosing equipment and biocides in use |
| 101-999 cfu/l | Carry out an on-line disinfection in conjunction with the Written Scheme. Review control measures and Risk Assessment. |
| > 1000 cfu/l | Carry out a full clean of system. Review control measures and Risk Assessment. |

- Hot & Cold Water systems / Showers

| Results | Action |
| --- | --- |
| <100 cfu/l | No action - continue normal controls. |
| 100-1,000 cfu/l | Evidence of poor control. Take action to reduce the count (e.g. clean and disinfect) and re-test within 3 months. Systems with persistent +ve test results should be reviewed by the Dutyholder Review control measures and Risk Assessment. |
| >1,000 cfu/l | Take the system out of service immediately. Thoroughly clean and disinfect. Re-submit sample for analysis. DO NOT RETURN TO SERVICE UNTIL COUNTS ARE <1000. Improve routine control measures. Review control measures and Risk Assessment. |

Reporting of dangerous occurrences shall be carried out in accordance with the Policy on the Reporting of Accidents, Dangerous Occurrences and Occupational Ill Health.

6.6 Performance Reviews

All performance reviews shall be carried out set against the following KPI as a minimum:-

- Risk Assessments are current, and compliant with L8, Part 1 Section 38.

- Control measures are in place, effective and recorded.

- Test data is recorded and archived. L8, Part 1, Record-Keeping Section 66 to 69.

- Cooling Tower audit and Operational Assessment has been completed and any issues raised have been addressed.

7.0 DOCUMENT MANAGEMENT

7.1 Policy and Written Schemes

This policy and associated written scheme are to be made available for the Facilities Management Department  through the FM website.

Changes to the documents are to be made only by the FM Duty Holder and under approval of the FM Director & FM Health and Safety Committee.

7.2 Risk assessment

The risk assessments and reviews are to be kept in electronic format on the FM X drive for access for management, nominated deputies and project managers on a building by building basis.

The action plans associated with the risk assessments are also to be kept on the X drive.

The risk assessments may also be kept on a webbased system as provided by the competent persons undertaking the contract to provide the risk assessment.

The risk assessments will be made available to those outside the FM department on request.

7.3 Service records

The routine monitoring and maintenance results are to be kept in electronic format on  the FM X drive on a contract by contract basis.

The service records will be made available to those outside the FM department on request.

Service and monitoring records provided by others for systems at LU will be held on the FM X drive.

8.0 VERSION CONTROL

| Version | Description of Change | Changed By | Date |
| --- | --- | --- | --- |
| 01d | Replaced Annex ‘O’ as a result of a comprehensive review of site systems and procedures | Claire Collier | 01/10/2010 |
| 02d | Amendments to Nominated Deputy roles | Claire Collier | 1/11/2010 |
| 03d | Amendments with comments from ND’s | Claire Collier | 17/11/2010 |
| 04d | Amendments to ND - Projects | Claire Collier | 22/11/2010 |
| 05d | Amendments to FM Project managers | Claire Collier | Mar 2011 |
| 06d | Amendments to role descriptions and formatting | Claire Collier | 9 Nov 2011 |
| 01 | Final issue | Claire Collier | 13 Feb 2012 |

# Text boxes

Vice Chancellor

(LU Duty Holder)

Health, Safety & Environment Manager

Associated Company Director – section, tenant

Deans of Schools

Director of FM

Nominated Responsible Person (Operation Managers)

Nominated Responsible Person

FM Duty Holder (Responsible Person)

Nominated Deputies

(Competent Persons)

Nominated Deputies

(Competent Persons)

FM Nominated Deputies (Competent persons)